## A2W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | 2
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | 1
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 2.05 | 1.9 | 1.88 | 2.13 | 2.08 | 1.95 | 2.33 | 2.05
2 | Ambient WB | ℃ | 0.55 | 0.48 | 0.38 | 0.8 | 0.85 | 0.63 | 1.1 | 0.69
3 | RH | % | 91.2 | 89.3 | 91.78 | 94.35 | 93.65 | 93.73 | 95.33 | 92.78
4 | Inlet Hot Water | ℃ | 29.68 | 29.75 | 29.88 | 30 | 30.1 | 30.13 | 30.18 | 29.95
5 | Outlet Hot Water | ℃ | 34.75 | 34.75 | 34.83 | 35 | 35.1 | 35.1 | 35.18 | 34.95
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.25 | 2.25 | 2.24 | 2.25 | 2.25 | 2.26 | 2.26 | 2.25
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 13295.47 | 13170.71 | 13110.21 | 13155.3 | 13198.62 | 13176.82 | 13242.53 | 13192.81
11 | Voltage | V | 386.38 | 384.18 | 382.67 | 383.7 | 381.15 | 380.59 | 382.62 | 382.48
12 | Current | A | 7.58 | 7.97 | 7.76 | 7.87 | 7.96 | 7.81 | 7.86 | 7.88
13 | Power Input | W | 3870.94 | 3911.86 | 3904.8 | 3916.02 | 3929.12 | 3910.38 | 3912.59 | 3911.45
14 | Power Factor | % | 0.76 | 0.74 | 0.76 | 0.75 | 0.75 | 0.76 | 0.75 | 0.75
15 | Frequency | Hz | 49.98 | 50 | 50 | 50 | 49.98 | 49.98 | 50.02 | 49.99
16 | COP | W/W | 3.4347 | 3.3669 | 3.3575 | 3.3594 | 3.3592 | 3.3697 | 3.3846 | 3.38
17 | Test Time | Sec | 4210 | 4270 | 4330 | 4390 | 4450 | 4510 | 4570 | ——
18 | Consumption | kW.h | 4.87 | 4.94 | 5 | 5.07 | 5.13 | 5.2 | 5.26 | ——
19 | Discharge Gas Temp | ℃ | 52.75 | 52.96 | 53.73 | 54.12 | 54.46 | 55.03 | 55.09 | 54.05
20 | Condenser Outlet Temp | ℃ | 33.04 | 33.05 | 32.65 | 33.1 | 33.38 | 32.72 | 33.38 | 32.99
21 | Evaporator Inlet Temp | ℃ | -6.17 | -6.5 | -6.62 | -6.16 | -6.34 | -6.75 | -6.17 | -6.38
22 | Evaporator Outlet Temp | ℃ | -4.71 | -5.13 | -4.7 | -4.75 | -6.25 | -4.8 | -4.63 | -4.66
23 | Suction Temp | ℃ | -4.39 | -4.54 | -3.12 | -2 | -2.57 | -2.5 | -1.58 | -2.86

## A2W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. |  | LSQ03RC-20081226-0001（R404A） |  |  |  | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | 2
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | 1
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 2.13 | 1.93 | 2.23 | 2.3 | 1.98 | 2.23 | 2.33 | 2.16
2 | Ambient WB | ℃ | 1.1 | 0.83 | 1.08 | 1.25 | 0.9 | 1.05 | 1.25 | 1.07
3 | RH | % | 96.3 | 96.15 | 96.68 | 96.75 | 96.35 | 96.8 | 96.68 | 96.52
4 | Inlet Hot Water | ℃ | 45.34 | 45.15 | 45 | 44.95 | 44.88 | 44.8 | 44.83 | 45.01
5 | Outlet Hot Water | ℃ | 50.03 | 49.85 | 49.75 | 49.65 | 49.57 | 49.5 | 49.53 | 49.72
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.11 | 2.11 | 2.11 | 2.11 | 2.1 | 2.1 | 2.1 | 2.11
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 11511.32 | 11520.36 | 11656.72 | 11520.36 | 11457.24 | 11479.36 | 11557.24 | 11521.13
11 | Voltage | V | 376.32 | 377.48 | 382.36 | 381.5 | 377.05 | 377.65 | 377.4 | 378.71
12 | Current | A | 9.72 | 9.7 | 9.46 | 9.43 | 9.7 | 9.43 | 9.4 | 9.53
13 | Power Input | W | 5280.81 | 5281.01 | 5241.14 | 5217.56 | 5235.74 | 5201.72 | 5220.14 | 5234.7
14 | Power Factor | % | 0.84 | 0.83 | 0.84 | 0.84 | 0.83 | 0.84 | 0.84 | 0.84
15 | Frequency | Hz | 50 | 49.98 | 50 | 50 | 50 | 50.02 | 50.02 | 50
16 | COP | W/W | 2.18 | 2.18 | 2.22 | 2.21 | 2.17 | 2.21 | 2.22 | 2.2
17 | Test Time | Sec | 6810 | 6870 | 6930 | 6990 | 7050 | 7110 | 7170 | ——
18 | Consumption | kW.h | 7.16 | 7.25 | 7.34 | 7.42 | 7.51 | 7.6 | 7.69 | ——
19 | Discharge Gas Temp | ℃ | 62.99 | 63.27 | 62.93 | 62.96 | 63.33 | 63.09 | 63.08 | 63.09
20 | Condenser Outlet Temp | ℃ | 49.43 | 49.26 | 49.16 | 49.07 | 48.91 | 48.93 | 48.91 | 49.09
21 | Evaporator Inlet Temp | ℃ | -2.24 | -2.45 | -1.97 | -2.07 | -2.55 | -2.15 | -2.17 | -2.23
22 | Evaporator Outlet Temp | ℃ | -4.68 | -4.86 | -4.32 | -4.4 | -4.92 | -4.49 | -4.52 | -4.6
23 | Suction Temp | ℃ | -6.3 | -6.46 | -5.95 | -6.11 | -6.59 | -6.16 | -6.21 | -6.25

## A-15W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | -15
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | -16
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -14.95 | -14.93 | -15.06 | -14.98 | -14.98 | -14.93 | -15.01 | -14.97
2 | Ambient WB | ℃ | -15.71 | -15.98 | -16.05 | -15.9 | -15.97 | -15.91 | -15.99 | -15.99
3 | RH | % | 67.6 | 67.18 | 66.45 | 66.68 | 67.58 | 67.83 | 67.75 | 67.31
4 | Inlet Hot Water | ℃ | 29.8 | 29.75 | 29.73 | 29.88 | 29.9 | 29.95 | 29.93 | 29.86
5 | Outlet Hot Water | ℃ | 34.4 | 34.18 | 34.05 | 34.08 | 34.2 | 34.2 | 34.28 | 34.24
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39 | 1.39
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 7449.95 | 7153.66 | 6992 | 6789.92 | 6951.58 | 6870.75 | 7032.42 | 7056.89
11 | Voltage | V | 386.38 | 383.62 | 382.88 | 382.92 | 383.79 | 385.26 | 385.13 | 384.41
12 | Current | A | 7.36 | 7.31 | 7.33 | 7.38 | 7.37 | 7.36 | 7.36 | 7.35
13 | Power Input | W | 3751.09 | 3735.61 | 3736.1 | 3733.94 | 3739.72 | 3745.2 | 3750.18 | 3742.47
14 | Power Factor | % | 0.76 | 0.77 | 0.77 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
15 | Frequency | Hz | 50.04 | 49.98 | 49.98 | 50 | 49.98 | 49.98 | 50.02 | 50
16 | COP | W/W | 1.99 | 1.91 | 1.87 | 1.82 | 1.86 | 1.83 | 1.88 | 1.89
17 | Test Time | Sec | 15050 | 15110 | 15170 | 15230 | 15290 | 15350 | 15410 | ——
18 | Consumption | kW.h | 16.73 | 16.79 | 16.85 | 16.92 | 16.98 | 17.04 | 17.1 | ——
19 | Discharge Gas Temp | ℃ | 49.1 | 49.01 | 49.09 | 49.25 | 49.31 | 49.32 | 49.4 | 49.21
20 | Condenser Outlet Temp | ℃ | 32.87 | 32.73 | 32.67 | 32.76 | 32.82 | 32.92 | 32.97 | 32.83
21 | Evaporator Inlet Temp | ℃ | -17.98 | -18.04 | -18.41 | -18.65 | -18.6 | -18.53 | -18.55 | -18.35
22 | Evaporator Outlet Temp | ℃ | -20.55 | -20.22 | -20.62 | -20.88 | -20.81 | -20.75 | -20.8 | -20.56
23 | Suction Temp | ℃ | -21.96 | -21.63 | -22.03 | -22.23 | -22.21 | -22.15 | -22.21 | -21.96

## A-15W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | -15
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | -16
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -14.93 | -14.9 | -14.98 | -14.95 | -15.01 | -15.04 | -15.03 | -14.98
2 | Ambient WB | ℃ | -16.03 | -16.01 | -16.07 | -16.05 | -16.08 | -16.13 | -16.08 | -16.07
3 | RH | % | 71.38 | 71.23 | 71.35 | 71.23 | 77.63 | 74.83 | 72.5 | 72.92
4 | Inlet Hot Water | ℃ | 45.05 | 45.03 | 45.05 | 45.08 | 45 | 44.98 | 44.9 | 45.04
5 | Outlet Hot Water | ℃ | 49.23 | 49.17 | 49.28 | 49.25 | 49.2 | 49.15 | 49.08 | 49.23
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 6605.28 | 6481.19 | 6601.86 | 6547.48 | 6580.92 | 6535.56 | 6523.35 | 6553.66
11 | Voltage | V | 385.39 | 384.22 | 385.17 | 385.91 | 386.08 | 385.91 | 386.38 | 385.64
12 | Current | A | 9.11 | 9.1 | 9.07 | 9.03 | 9.04 | 9.03 | 9.01 | 9.06
13 | Power Input | W | 5098.65 | 5088.51 | 5064.33 | 5044.19 | 5048.88 | 5041.28 | 5030.05 | 5059.68
14 | Power Factor | % | 0.84 | 0.84 | 0.84 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
15 | Frequency | Hz | 50.04 | 50 | 50.02 | 50 | 50 | 50.02 | 50.02 | 50.01
16 | COP | W/W | 1.2955 | 1.2737 | 1.3036 | 1.298 | 1.3034 | 1.2964 | 1.2969 | 1.29
17 | Test Time | Sec | 16930 | 16990 | 17050 | 17110 | 17170 | 17230 | 17290 | ——
18 | Consumption | kW.h | 18.93 | 19.02 | 19.1 | 19.19 | 19.27 | 19.35 | 19.44 | ——
19 | Discharge Gas Temp | ℃ | 67.4 | 67.56 | 67.66 | 67.53 | 67.13 | 67.14 | 67.33 | 67.39
20 | Condenser Outlet Temp | ℃ | 46.88 | 46.81 | 46.74 | 46.6 | 46.64 | 46.55 | 46.46 | 46.66
21 | Evaporator Inlet Temp | ℃ | -15.05 | -15.06 | -15.15 | -15.17 | -14.73 | -14.94 | -15.13 | -15.03
22 | Evaporator Outlet Temp | ℃ | -18.02 | -18.03 | -18.12 | -18.15 | -17.73 | -17.92 | -18.1 | -18
23 | Suction Temp | ℃ | -19.44 | -19.44 | -19.53 | -19.59 | -19.14 | -19.36 | -19.53 | -19.42

## A-7W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | 380V 3Ph
File No. |  | LSQ05RC |  |  |  | Rated Voltage(V) |  | 220V 1Ph
Model No. |  | LSQ03RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | 3800g |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 2500 |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | -7
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | -8
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -7.05 | -7.1 | -7.1 | -7.08 | -6.93 | -6.93 | -6.95 | -7.01
2 | Ambient WB | ℃ | -8.04 | -8.07 | -8.09 | -7.99 | -7.74 | -7.83 | -7.69 | -7.91
3 | RH | % | 72.1 | 72.43 | 71.88 | 74.03 | 76.95 | 74.63 | 79.2 | 74.52
4 | Inlet Hot Water | ℃ | 30.2 | 30.18 | 30.05 | 29.98 | 29.95 | 29.95 | 29.9 | 30.03
5 | Outlet Hot Water | ℃ | 34.98 | 34.93 | 34.88 | 34.8 | 34.8 | 34.75 | 34.7 | 34.84
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.69
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 10399.23 | 10250.09 | 9797.8 | 9883.85 | 9932.98 | 9948.66 | 9848.66 | 10008.7
11 | Voltage | V | 388.5 | 386.94 | 384.05 | 384.48 | 385.08 | 384.87 | 385.13 | 385.56
12 | Current | A | 7.73 | 7.67 | 7.59 | 7.54 | 7.54 | 7.56 | 7.56 | 7.61
13 | Power Input | W | 3788.21 | 3773.42 | 3755.06 | 3747.94 | 3756.47 | 3754.35 | 3760.39 | 3762.26
14 | Power Factor | % | 0.75 | 0.75 | 0.76 | 0.77 | 0.77 | 0.76 | 0.76 | 0.76
15 | Frequency | Hz | 50 | 49.98 | 50.02 | 50.02 | 50.02 | 50.04 | 50 | 50.01
16 | COP | W/W | 2.7452 | 2.7164 | 2.6092 | 2.6371 | 2.6442 | 2.6499 | 2.6191 | 2.66
17 | Test Time | Sec | 11850 | 11910 | 11970 | 12030 | 12090 | 12150 | 12210 | ——
18 | Consumption | kW.h | 13 | 13.07 | 13.13 | 13.19 | 13.26 | 13.32 | 13.39 | ——
19 | Condenser inlet Temp | ℃ | 49.03 | 48.93 | 48.88 | 48.82 | 48.53 | 48.65 | 48.58 | 48.77
20 | Condenser Outlet Temp | ℃ | 34.2 | 34.17 | 34.08 | 33.96 | 33.92 | 33.87 | 33.87 | 34.01
21 | Evaporator Inlet Temp | ℃ | -13.18 | -13.18 | -13.19 | -13.15 | -12.84 | -13.07 | -12.87 | -13.06
22 | Evaporator Outlet Temp | ℃ | -15.24 | -15.23 | -15.23 | -15.17 | -14.83 | -15.07 | -14.88 | -15.09
23 | Suction Temp | ℃ | -16.7 | -16.68 | -16.71 | -16.62 | -16.31 | -16.57 | -16.32 | -16.55

## A-7W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | -7
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | -8
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -7.03 | -7 | -7 | -7.08 | -7.08 | -7 | -6.95 | -7.02
2 | Ambient WB | ℃ | -7.97 | -7.96 | -7.97 | -8.03 | -8.03 | -7.97 | -7.85 | -7.97
3 | RH | % | 73.18 | 72.93 | 72.75 | 72.85 | 72.88 | 72.65 | 74.68 | 73.22
4 | Inlet Hot Water | ℃ | 44.8 | 44.83 | 45.03 | 45.1 | 45.15 | 45.18 | 45.1 | 45.03
5 | Outlet Hot Water | ℃ | 49.21 | 49.28 | 49.59 | 49.56 | 49.55 | 49.58 | 49.6 | 49.48
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 1.48 | 1.49 | 1.49 | 1.49 | 1.48 | 1.48 | 1.48 | 1.48
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 8573.82 | 8412.76 | 8326.69 | 8416.69 | 8286.32 | 8373.82 | 8459.03 | 8407.02
11 | Voltage | V | 387.46 | 387.5 | 387.98 | 387.85 | 387.42 | 387.33 | 387.2 | 387.21
12 | Current | A | 9.22 | 9.2 | 9.23 | 9.26 | 9.25 | 9.24 | 9.27 | 9.26
13 | Power Input | W | 5123.3 | 5123.02 | 5155.23 | 5170.45 | 5174.53 | 5175.79 | 5173.85 | 5157.66
14 | Power Factor | % | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
15 | Frequency | Hz | 50 | 50 | 50.04 | 50.02 | 50 | 49.98 | 50 | 50.01
16 | COP | W/W | 1.6735 | 1.6421 | 1.6152 | 1.6278 | 1.6014 | 1.6179 | 1.635 | 1.63
17 | Test Time | Sec | 13350 | 13410 | 13470 | 13530 | 13590 | 13650 | 13710 | ——
18 | Consumption | kW.h | 14.79 | 14.87 | 14.96 | 15.05 | 15.13 | 15.22 | 15.31 | ——
19 | Discharge Gas Temp | ℃ | 63.7 | 63.74 | 63.98 | 64.41 | 64.58 | 64.52 | 64.53 | 64.2
20 | Condenser Outlet Temp | ℃ | 47.67 | 47.74 | 47.92 | 48.08 | 48.15 | 48.15 | 48.16 | 47.98
21 | Evaporator Inlet Temp | ℃ | -9.48 | -9.49 | -9.46 | -9.48 | -9.44 | -9.43 | -9.35 | -9.44
22 | Evaporator Outlet Temp | ℃ | -12.33 | -12.32 | -12.32 | -12.37 | -12.32 | -12.32 | -12.17 | -12.3
23 | Suction Temp | ℃ | -13.94 | -13.94 | -13.94 | -13.97 | -13.93 | -13.92 | -13.79 | -13.91

## A-2W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | -2
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | -3
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -2.28 | -2.28 | -2.2 | -2.2 | -2.15 | -2.05 | -2.15 | -2.19
2 | Ambient WB | ℃ | -3.26 | -3.26 | -3.2 | -3.23 | -3.14 | -3.05 | -3.17 | -3.19
3 | RH | % | 78.9 | 79 | 78.8 | 78.2 | 79 | 78.98 | 78.28 | 78.75
4 | Inlet Hot Water | ℃ | 30.25 | 30.25 | 30.15 | 29.95 | 29.9 | 29.88 | 29.9 | 30.1
5 | Outlet Hot Water | ℃ | 35.08 | 35.05 | 35.08 | 34.9 | 34.78 | 34.79 | 34.78 | 34.89
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11 | 2.11
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 11801.7 | 11779.43 | 12071.64 | 12133 | 11963.48 | 11929.1 | 11788.62 | 11856.06
11 | Voltage | V | 381.84 | 383.57 | 380.38 | 379.21 | 378.95 | 379.51 | 380.03 | 380.39
12 | Current | A | 7.78 | 7.64 | 7.62 | 7.6 | 7.54 | 7.52 | 7.55 | 7.63
13 | Power Input | W | 3892.29 | 3952.02 | 3920.02 | 3857.73 | 3819.74 | 3829.21 | 3815.58 | 3868.89
14 | Power Factor | % | 0.76 | 0.78 | 0.78 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77
15 | Frequency | Hz | 50.02 | 50 | 50.02 | 50.04 | 50.02 | 50.02 | 50.02 | 50.02
16 | COP | W/W | 3.01 | 2.98 | 3.08 | 3.15 | 3.13 | 3.05 | 2.99 | 3.02
17 | Test Time | Sec | 9090 | 9150 | 9210 | 9270 | 9330 | 9390 | 9450 | ——
18 | Consumption | kW.h | 9.53 | 9.6 | 9.66 | 9.73 | 9.79 | 9.85 | 9.92 | ——
19 | Discharge Gas Temp | ℃ | 48.78 | 49.74 | 50.05 | 50.26 | 50.27 | 50.44 | 50.66 | 50
20 | Condenser Outlet Temp | ℃ | 34.79 | 34.58 | 34.2 | 33.84 | 33.56 | 33.4 | 33.52 | 33.99
21 | Evaporator Inlet Temp | ℃ | -9.37 | -9.37 | -9.42 | -9.54 | -9.5 | -9.52 | -9.61 | -9.47
22 | Evaporator Outlet Temp | ℃ | -11.19 | -11.14 | -11.15 | -11.24 | -11.12 | -11.17 | -11.27 | -11.17
23 | Suction Temp | ℃ | -11.4 | -10.88 | -10.49 | -10.33 | -10.15 | -9.74 | -10.07 | -10.47

## A-2W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | -2
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | -3
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | -1.9 | -1.9 | -1.93 | -2 | -2.03 | -2.05 | 2.09 | -1.98
2 | Ambient WB | ℃ | -2.91 | -2.91 | -2.94 | -3 | -3.04 | -3.06 | -3.11 | -2.99
3 | RH | % | 79.2 | 79.13 | 78.93 | 79.1 | 78.93 | 78.85 | 78.85 | 79.01
4 | Inlet Hot Water | ℃ | 44.93 | 45.05 | 45.03 | 45.08 | 45.03 | 44.98 | 44.93 | 45.01
5 | Outlet Hot Water | ℃ | 49.46 | 49.58 | 49.6 | 49.64 | 49.57 | 49.45 | 49.48 | 49.54
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 1.96 | 1.96 | 1.96 | 1.95 | 1.95 | 1.96 | 1.95 | 1.96
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 10218.36 | 10175.35 | 10305.07 | 10294.34 | 10275.6 | 10178.29 | 10273.41 | 10235.13
11 | Voltage | V | 378.86 | 379.04 | 379.73 | 379.47 | 378.78 | 379.94 | 380.16 | 379.24
12 | Current | A | 9.46 | 9.51 | 9.53 | 9.57 | 9.54 | 9.41 | 9.34 | 9.49
13 | Power Input | W | 5239.07 | 5273.68 | 5293.24 | 5299.22 | 5258.14 | 5182.33 | 5150.21 | 5241.43
14 | Power Factor | % | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
15 | Frequency | Hz | 50.04 | 50.02 | 50.02 | 49.98 | 49.96 | 49.98 | 50 | 50
16 | COP | W/W | 1.94 | 1.93 | 1.95 | 1.95 | 1.96 | 1.95 | 1.97 | 1.95
17 | Test Time | Sec | 10130 | 10190 | 10250 | 10310 | 10370 | 10430 | 10490 | ——
18 | Consumption | kW.h | 10.81 | 10.9 | 10.99 | 11.08 | 11.17 | 11.25 | 11.34 | ——
19 | Discharge Gas Temp | ℃ | 58.69 | 59.08 | 59.26 | 59.38 | 59.2 | 58.49 | 57.67 | 58.79
20 | Condenser Outlet Temp | ℃ | 48.45 | 48.81 | 49.1 | 49.2 | 49.07 | 48.81 | 48.65 | 48.85
21 | Evaporator Inlet Temp | ℃ | -4.91 | -4.86 | -4.85 | -4.87 | -4.92 | -5.01 | -5.13 | -4.94
22 | Evaporator Outlet Temp | ℃ | -7.55 | -7.5 | -7.5 | -7.53 | -7.62 | -7.69 | -7.8 | -7.61
23 | Suction Temp | ℃ | -9.49 | -9.44 | -9.46 | -9.51 | -9.6 | -9.7 | -9.86 | -9.59

## A7W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | 7
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | 6
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 7.73 | 7.73 | 7.55 | 7.2 | 7.08 | 7.03 | 7.23 | 7.37
2 | Ambient WB | ℃ | 6.28 | 6.1 | 5.98 | 5.53 | 5.53 | 5.45 | 5.8 | 5.82
3 | RH | % | 91.4 | 90.08 | 89.15 | 88.73 | 90.4 | 90.5 | 92.78 | 90.56
4 | Inlet Hot Water | ℃ | 30.3 | 30.33 | 30.18 | 30.13 | 30.08 | 30.03 | 29.85 | 30.12
5 | Outlet Hot Water | ℃ | 35.2 | 35.25 | 35.18 | 35.03 | 34.93 | 34.88 | 34.8 | 35.03
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.67 | 2.66 | 2.66 | 2.66 | 2.66 | 2.66 | 2.67 | 2.66
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 15987.76 | 15836.61 | 15754.39 | 15831.35 | 15890.33 | 15604.87 | 15942.74 | 15835.42
11 | Voltage | V | 387.37 | 384.31 | 381.84 | 381.76 | 383.4 | 388.02 | 393.34 | 385.85
12 | Current | A | 7.79 | 7.77 | 7.69 | 7.78 | 7.92 | 7.95 | 7.58 | 7.8
13 | Power Input | W | 3947.52 | 3937.36 | 3923.32 | 3925.12 | 3937.85 | 3940.66 | 3881.1 | 3927.47
14 | Power Factor | % | 0.75 | 0.76 | 0.77 | 0.76 | 0.75 | 0.74 | 0.75 | 0.75
15 | Frequency | Hz | 50 | 50 | 50.02 | 50.04 | 50 | 50 | 50.02 | 50.01
16 | COP | W/W | 4.0501 | 4.0221 | 4.0156 | 4.0333 | 4.0353 | 3.96 | 4.1078 | 4.03
17 | Test Time | Sec | 870 | 930 | 990 | 1050 | 1110 | 1170 | 1230 | ——
18 | Consumption | kW.h | 0.98 | 1.05 | 1.11 | 1.18 | 1.24 | 1.31 | 1.38 | ——
19 | Discharge Gas Temp | ℃ | 55.33 | 55.38 | 55.31 | 55.46 | 55.37 | 55.37 | 55.26 | 55.35
20 | Condenser Outlet Temp | ℃ | 35.13 | 34.87 | 34.8 | 34.17 | 34.33 | 34.46 | 34.66 | 34.63
21 | Evaporator Inlet Temp | ℃ | -1.65 | -1.85 | -2.02 | -2.62 | -2.65 | -2.75 | -2.42 | -2.27
22 | Evaporator Outlet Temp | ℃ | -0.07 | -0.09 | -0.41 | -0.83 | -0.9 | -1.22 | -0.7 | -0.6
23 | Suction Temp | ℃ | 3.06 | 2.69 | 2.51 | 1.84 | 1.97 | 1.9 | 2.44 | 2.38

## A7W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | 7
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | 6
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 7.08 | 7.1 | 7.4 | 7.18 | 7.1 | 7.38 | 7.23 | 7.2
2 | Ambient WB | ℃ | 5.83 | 5.78 | 6.18 | 5.95 | 5.8 | 6.18 | 6.08 | 5.96
3 | RH | % | 93.38 | 93.9 | 94.9 | 93.8 | 94.08 | 95.15 | 94.63 | 94.25
4 | Inlet Hot Water | ℃ | 45.13 | 45.18 | 44.88 | 44.88 | 44.68 | 44.93 | 45.13 | 45.03
5 | Outlet Hot Water | ℃ | 50.01 | 50.05 | 49.83 | 49.75 | 49.48 | 49.76 | 49.89 | 49.79
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.5 | 2.51 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 14188.27 | 14217.19 | 14392.81 | 14188.99 | 13983.66 | 13920.52 | 13975.14 | 14132.16
11 | Voltage | V | 389.71 | 391.05 | 395.8 | 396.45 | 393.6 | 397.22 | 394.24 | 394.37
12 | Current | A | 9.81 | 9.78 | 9.31 | 9.52 | 9.75 | 9.35 | 9.53 | 9.57
13 | Power Input | W | 5333.13 | 5324.11 | 5231.65 | 5235.5 | 5267.98 | 5232.39 | 5264.36 | 5268.68
14 | Power Factor | % | 0.8 | 0.8 | 0.82 | 0.8 | 0.79 | 0.81 | 0.81 | 0.81
15 | Frequency | Hz | 50 | 50 | 50.02 | 50.04 | 50.06 | 50.02 | 49.98 | 50.01
16 | COP | W/W | 2.65 | 2.67 | 2.75 | 2.71 | 2.64 | 2.63 | 2.64 | 2.67
17 | Test Time | Sec | 2690 | 2750 | 2810 | 2870 | 2930 | 2990 | 3050 | ——
18 | Consumption | kW.h | 2.97 | 3.06 | 3.14 | 3.23 | 3.32 | 3.41 | 3.49 | ——
19 | Discharge Gas Temp | ℃ | 63.16 | 63.02 | 62.47 | 62.58 | 62.46 | 62.3 | 62.72 | 62.69
20 | Condenser Outlet Temp | ℃ | 50.01 | 49.82 | 49.52 | 49.31 | 49.26 | 49.42 | 49.66 | 49.58
21 | Evaporator Inlet Temp | ℃ | 1.52 | 1.67 | 2.01 | 1.56 | 1.62 | 2.07 | 1.72 | 1.73
22 | Evaporator Outlet Temp | ℃ | -0.7 | -0.52 | -0.13 | -0.63 | -0.55 | -0.09 | -0.45 | -0.45
23 | Suction Temp | ℃ | -2.34 | -2.17 | -1.83 | -2.31 | -2.18 | -1.78 | -2.15 | -2.12

## A10W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | 10
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | 9
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 10.08 | 10.03 | 10.05 | 10.03 | 10.02 | 10.05 | 10.03 | 10.05
2 | Ambient WB | ℃ | 8.75 | 8.5 | 8.83 | 8.93 | 8.48 | 8.58 | 9.03 | 8.74
3 | RH | % | 92.48 | 92.58 | 94.38 | 94.23 | 92.73 | 94.3 | 95.45 | 93.77
4 | Inlet Hot Water | ℃ | 30.05 | 30 | 29.9 | 29.93 | 29.85 | 29.73 | 29.8 | 29.9
5 | Outlet Hot Water | ℃ | 34.93 | 34.88 | 34.93 | 34.9 | 34.73 | 34.7 | 34.75 | 34.84
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.99 | 2.99 | 2.99 | 2.99 | 2.98 | 2.98 | 2.98 | 2.99
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 16939.03 | 16939.61 | 17460.66 | 17300.74 | 16909.96 | 17242.88 | 17170.19 | 17171.88
11 | Voltage | V | 374.03 | 375.49 | 378.91 | 377.09 | 375.58 | 376.23 | 379.64 | 376.55
12 | Current | A | 7.78 | 7.84 | 7.77 | 7.88 | 7.97 | 8.09 | 8.01 | 7.87
13 | Power Input | W | 3930.42 | 3927.62 | 3915.11 | 3912.9 | 3943.79 | 3946.28 | 3966.07 | 3926.92
14 | Power Factor | % | 0.78 | 0.77 | 0.77 | 0.76 | 0.76 | 0.75 | 0.75 | 0.76
15 | Frequency | Hz | 50.02 | 50.02 | 49.98 | 50 | 50.02 | 49.96 | 49.98 | 50
16 | COP | W/W | 4.32 | 4.32 | 4.46 | 4.42 | 4.29 | 4.37 | 4.33 | 4.38
17 | Test Time | Sec | 3610 | 3670 | 3730 | 3790 | 3850 | 3910 | 3970 | ——
18 | Consumption | kW.h | 4.41 | 4.47 | 4.54 | 4.6 | 4.67 | 4.73 | 4.8 | ——

## A10W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | 10
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | 9
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 10.25 | 10.28 | 10.15 | 9.93 | 10.25 | 10.18 | 10.23 | 10.18
2 | Ambient WB | ℃ | 9.15 | 9.23 | 8.75 | 8.25 | 8.83 | 9.35 | 9.23 | 8.97
3 | RH | % | 91.95 | 92.18 | 91.85 | 92.53 | 92.23 | 92.53 | 92.33 | 92.34
4 | Inlet Hot Water | ℃ | 45.05 | 45.08 | 45.1 | 45.08 | 44.97 | 44.96 | 44.89 | 45.04
5 | Outlet Hot Water | ℃ | 49.98 | 50.05 | 50.08 | 50.06 | 50.02 | 50 | 49.95 | 50.01
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 2.79 | 2.79 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 15981.26 | 16114.43 | 16085.93 | 16075.55 | 16113.13 | 16113.13 | 16147.42 | 16082.18
11 | Voltage | V | 376.92 | 376.44 | 372.86 | 372.34 | 375.93 | 378.43 | 375.97 | 375.59
12 | Current | A | 9.68 | 9.63 | 9.66 | 9.53 | 9.56 | 9.62 | 9.41 | 9.57
13 | Power Input | W | 5218.43 | 5253.4 | 5240.81 | 5210.48 | 5204.3 | 5224.8 | 5176.94 | 5216.78
14 | Power Factor | % | 0.83 | 0.84 | 0.84 | 0.85 | 0.84 | 0.83 | 0.84 | 0.84
15 | Frequency | Hz | 50 | 49.98 | 50 | 50 | 49.98 | 50 | 50 | 49.99
16 | COP | W/W | 3.07 | 3.07 | 3.07 | 3.07 | 3.08 | 3.08 | 3.1 | 3.08
17 | Test Time | Sec | 5010 | 5070 | 5130 | 5190 | 5250 | 5310 | 5370 | ——
18 | Consumption | kW.h | 6.19 | 6.28 | 6.36 | 6.45 | 6.54 | 6.62 | 6.71 | ——

## A20W35
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 30 |  | Ambient Temp Dry Bulb（℃） |  |  | 20
Outlet Water Temp（℃） |  |  |  | 35 |  | Ambient Temp Web Bulb（℃） |  |  | 15
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 20 | 20 | 20 | 20 | 20.03 | 20 | 20 | 20
2 | Ambient WB | ℃ | 14.85 | 14.73 | 14.7 | 15.05 | 14.9 | 14.8 | 15.1 | 14.88
3 | RH | % | 70.25 | 68.23 | 69.93 | 71.3 | 68.43 | 70.25 | 71.38 | 70
4 | Inlet Hot Water | ℃ | 30.12 | 30.13 | 30.08 | 30.1 | 30.1 | 30.08 | 30 | 30.08
5 | Outlet Hot Water | ℃ | 35.27 | 35.24 | 35.23 | 35.27 | 35.28 | 35.3 | 35.3 | 35.25
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 3.42 | 3.42 | 3.43 | 3.43 | 3.43 | 3.44 | 3.44 | 3.43
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 20582.66 | 20559.75 | 20602.63 | 20629.12 | 20639.36 | 20604.76 | 20579.95 | 20607.4
11 | Voltage | V | 382.23 | 381.63 | 381.8 | 383.62 | 382.84 | 382.75 | 384.09 | 383.25
12 | Current | A | 7.97 | 7.93 | 7.84 | 8.07 | 8 | 7.99 | 8.01 | 7.94
13 | Power Input | W | 4065.76 | 4050.1 | 3976.54 | 4058.57 | 4048.26 | 4025.61 | 4012.78 | 4036.5
14 | Power Factor | % | 0.77 | 0.77 | 0.77 | 0.76 | 0.76 | 0.76 | 0.75 | 0.76
15 | Frequency | Hz | 49.98 | 49.94 | 49.96 | 49.96 | 50 | 50 | 50 | 49.98
16 | COP | W/W | 5.05 | 5.06 | 5.08 | 5.09 | 5.1 | 5.08 | 5.06 | 5.07
17 | Test Time | Sec | 130 | 190 | 250 | 310 | 370 | 430 | 490 | ——
18 | Consumption | kW.h | 0.17 | 0.24 | 0.3 | 0.37 | 0.44 | 0.5 | 0.57 | ——

## A20W50
SIRAC LAB TEST REPORT
Item |  | Description |  |  |  | Item |  | Description
File No. | [5 empty] | Rated Voltage(V) |  | 380V 3Ph
Model No. |  | LSQ05RC |  |  |  | Rated Frequency(Hz) |  | 50
Serial No. | [5 empty] | Hot Water Volum(L)
Compressor No. | [5 empty] | Rated Heating Capacity (W)
Refrigerant Type |  | R404A |  |  |  | Rated Power Input(W)
Refrigerant Qnty(g) |  | 3800g |  |  |  | Tester
Flow Restriction |  | Expansion Valve |  |  |  | Test Date
Test Contidions
Item |  |  |  | Description |  | Item |  |  | Discription
Heat Pump Type |  |  |  | Air to Water |  | Test Conditions |  |  | Controlled
Inlet Water Temp（℃） |  |  |  | 45 |  | Ambient Temp Dry Bulb（℃） |  |  | 20
Outlet Water Temp（℃） |  |  |  | 50 |  | Ambient Temp Web Bulb（℃） |  |  | 15
Records
No. | Data Name | Unit | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Data 6 | Data 7 | Average
1 | Ambient DB | ℃ | 20.25 | 20.1 | 20 | 20 | 20 | 20 | 20 | 20.05
2 | Ambient WB | ℃ | 15.15 | 14.9 | 14.88 | 14.95 | 14.9 | 15 | 15 | 14.98
3 | RH | % | 67.58 | 67.2 | 68.3 | 68.55 | 68.23 | 68.78 | 67.85 | 68.04
4 | Inlet Hot Water | ℃ | 44.98 | 45 | 44.98 | 44.98 | 44.95 | 44.9 | 44.83 | 44.95
5 | Outlet Hot Water | ℃ | 50.1 | 50.13 | 50.15 | 50.13 | 50.1 | 50.05 | 50 | 50.09
6 | Inlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
7 | Outlet Cold Water | ℃ | —— | —— | —— | —— | —— | —— | —— | ——
8 | Hot Water Flow | m3/h | 3.19 | 3.19 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
9 | Cold Water Flow | m3/h | —— | —— | —— | —— | —— | —— | —— | ——
10 | Heating Capacity | W | 18985.72 | 18985.72 | 19124.41 | 19017.12 | 19017.12 | 19017.41 | 19109.88 | 19002.9
11 | Voltage | V | 383.27 | 382.15 | 381.54 | 381.76 | 382.88 | 383.27 | 383.05 | 382.72
12 | Current | A | 9.51 | 9.57 | 9.51 | 9.55 | 9.52 | 9.65 | 9.67 | 9.56
13 | Power Input | W | 5290.29 | 5299.43 | 5283.92 | 5289.96 | 5283.62 | 5291.52 | 5287.07 | 5290.14
14 | Power Factor | % | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.82 | 0.82 | 0.83
15 | Frequency | Hz | 49.98 | 50 | 49.98 | 50 | 49.98 | 50 | 50 | 49.99
16 | COP | W/W | 3.59 | 3.58 | 3.62 | 3.59 | 3.6 | 3.59 | 3.61 | 3.59
17 | Test Time | Sec | 1550 | 1610 | 1670 | 1730 | 1790 | 1850 | 1910 | ——
18 | Consumption | kW.h | 1.91 | 1.99 | 2.08 | 2.17 | 2.26 | 2.35 | 2.43 | ——